## Slide 2: Controller design and tuning
Wind Turbine Control Online Course
Alan Wai Hou Lio
Researcher, DTU Wind Energy
wali@dtu.dk

## Slide 3: Learning objectives
After this session you should be able to:
Understand how to maximise the power captured by a turbine
Describe what types of controllers are used in Region 2
Understand the design philosophy behind a generator torque controller in Region 2
Calculate the torque controller gain in Region 2

## Slide 4: Let’s control a wind turbine
Three actuators:
Blade pitch motor
Generator torque converter
Yaw motor
Sensors:
Generator/Rotor speed sensor
Anemometers
More actuators and sensors available for large turbine
Actuators: Trailing-edge flap
Sensors: LiDAR, tower and blade load sensors
Source: Pao et al. 2009

## Slide 5: Power in the wind
Power available in the wind
Power captured by wind turbine
: air density
: rotor radius
: wind speed
: Power coefficient
: tip-speed ratio
Region 1
Control Objectives:
(1) Optimize power production at below rated wind speeds (region 1)
(2) Limit power and loads at above rated wind speeds (region 3)
rotor speed

## Slide 6: Variable-speed Pitch-regulated control
Region 2
Region 2.5
Region 3
Region 2.5
Region 2
Region 3
Cp

## Slide 7: Region 2 controller design
Control objective: Maximising Cp by operating the turbine at and
Control input:
  pitch angle is kept at optimal =
  Generator torque such that
If we know the wind speed , we can track the optimal tip-speed ratio using a PI controller.
But what if we don’t know ?
Wind turbine
PI Controller

## Slide 8: Region 2 Problem with wind measurement
Wind speed measurement
  Wind cup: subject to noise
  Lidar: expensive
LiDAR
Wind anemometer
Can we track the optimal Cp (or optimal tip-speed ratio) without using the wind speed measurement?

## Slide 9: Region 2 controller design
Consider the power law and the optimal power
Substituting the tip-speed ratio
In terms of electrical power
Neglect transient response, then Qe becomes:
: generator torque at LSS
: efficiency

## Slide 10: Region 2: Alternative form
On the Low-Speed Side (LSS)
On the High-Speed Side (HSS)
Thus,
IMPORTANT
In the Matlab code, we consider the rotor speed and generator torque on the LSS.
: generator torque at HSS
: generator speed
: gear-box ratio

## Slide 11: Region 2: Optimal Cp tracking
Strategy: Keep pitch angle at optimum and use generator torque to obtain optimal tip speed ratio in a torque equilibrium
Rotor inertia
Rotor speed
Rotor torque
Gearbox ratio
Generator torque
Region 1

## Slide 12: Region 2: Derivation of generator torque constant
Go through derivation (Lecture notes)

## Slide 13: Region 2: Cp tracking – Transient behaviour
What will happen to the Cp, and when the turbine see a wind gust?
Consider the nonlinear equation of drivetrain motion:
From the wind power law, we know that:
Assume the generator torque on the low-speed side is set as follows:
Substituting Q and Qg into the nonlinear equation :
Rotor inertia
Generator inertia
Rotor speed
Rotor torque
Gearbox ratio
Generator torque
Newton’s second law

## Slide 14: Region 2: Cp tracking - Analysis
Based on the nonlinear equation,
  the rotor will accelerate if , or equivalently ;
  the rotor will decelerate if , or equivalently ;
  the rotor will remain constant if , or equivalently .

## Slide 15: Region 2: Cp tracking - Transient behaviour
Cp surface
Rotor accelerates when
Rotor decelerates when
Region 2
Region 2.5
Region 3
Cp
/

## Slide 16: Region 2: Cp tracking - Analysis
Imagine the turbine operating a steady-state ( when a gust hits the turbine
Rotor speed does not change instantaneously due to large inertia
, turbine operating at the left section of the figure
From the figure, we know that the rotor will accelerate
if
if overshoot,
Higher rotor speed,
Higher torques,
Higher power
From the figure, we know that the rotor will decelerate

## Slide 17: Region 2: Optimal Cp tracking
Exercise: Region 2 controller
Open part_3.m, and run InitWT_10MW to find the parameters
Calculate the value for Kopt
  Can you get the steady-state Cp value?
  How close can you get to the actual optimal Cp,max?

## Slide 18: Region 2: Optimal Cp tracking
Kopt = 9.8182e+06 Nm
Why Cp =/= Cp,max 0.4935?

## Slide 19: Region 1: Optimal Cp tracking
Because and degree for this turbine model
Exercise: Region 2 controller
In InitWT_10MW, change controller.minPitch = -1
In wpdata_DTU10MW.100, change it as follows.
Re-run part_3.m

## Slide 20: Region 2: Optimal Cp tracking
Now, Cp = Cp,max (0.4935)

## Slide 21: Summary
By now, we should be able to:
  Explain the reason behind the generator torque controller design
  Describe the generator torque design in Region 2
  Calculate the gain for the generator torque controller