## Slide 2: Controller design and tuning: Region 2.5 and 3
Wind Turbine Control Online Course
Alan Wai Hou Lio
Researcher, DTU Wind Energy
wali@dtu.dk

## Slide 3: Re-cap
Three operational regions.
Region 2 Controller:
Transient analysis:
Region 2.5
Region 2
Region 3
Region 2
Region 2.5
Region 3
Cp

## Slide 4: Reading materials
https://github.com/alanliowh/Control_Online_Course
Updated files
https://github.com/alanliowh/Control_Online_Course

## Slide 5: Learning objectives
After this session you should be able to:
Describe what types of controllers are used in Region 2.5 and 3.
Tune a PI pitch and torque controller in Region 2.5 and 3
Calculate aerodynamic gain scheduling for Region 3

## Slide 6: Second-order mass-spring-damper system
Consider a mass-spring-damper system:
Standard form:
Solution of the second-order system
Newton’s second law
: natural frequency
: damping ratio
Damped natural frequency
Remember that the drive-train is a second-order system

## Slide 7: Region 2.5: Speed regulation
Strategy: Use generator torque (and pitch) to regulate rotor speed to the rated speed

## Slide 8: Region 2.5: Speed regulation
Nonlinear equation of motion of drivetrain dynamic:
Generator torque behaves like a PI controller:
Pitch controller also behaves like a PI controller
  Since it’s the same in Region 3, let’s discuss later
  For simplicity, in the analysis we assume
Now, we need to tune Kp and Ki
+
Lecture notes
Control input

## Slide 9: Region 2.5: Linearisation
Consider the drive-train equation
Let’s linearise it, and define the operating point and deviations
Substituting the derivations into the drive-train equation
Thus, the linearised equation becomes:
…
Taylor series expansion
From previous slide
)

## Slide 10: Region 2.5: Analysis
Linearised equation of drive-train
Closed-loop equation as second-order system
)
mass
damping
stiffness
External force

## Slide 11: Region 2: Speed regulation
The linearized closed-loop controller equation
Exercise: Calculate the and
Write the equation in standard form (, tip: assuming ).
What are the natural frequency and damping coefficient in terms of ?
Use your two equations from Eqn 2 to calculate kPg and kIg in terms of
mass
damping
stiffness
External force

## Slide 12: Region 2.5: Exercise answer
Sometimes, we assume = 0 negligible

## Slide 13: Region 2.5: Pole-placement
Rule of thumb:
Higher , “faster” reponse
Higher , less overshoot
Engineers can freely choose the behaviour of the closed-loop speed mode.
Remember: the response oscillates at the damped natural frequency

## Slide 14: Region 2.5: Pole-placement
Speed regulator mode frequency should be :
  Not too low to avoid large rotor speed oscillation
  Not too high to avoid tower excitation
mass
damping
stiffness
External force
Damped natural frequency

## Slide 15: Region 2.5 : Exercise
DTU 10MW
  tower natural frequency = 0.25 Hz (turbine.omega_t in rad/s)
Exercise: Calculate the and
Open Part_4.m
Calculate the and , assuming and = 0
Calculate another set of and , assuming and = 0
What do you see?
turbine.neff = 0.94;
turbine.J= 0.1570966689E+09;

## Slide 16: Region 2.5: Answer
controller.Kp25 = 6.4949e7 ;
controller.Ki25 = 1.4575e7;
controller.Kp25 = 2.598e8 ;
controller.Ki25 = 2.33e8;

## Slide 17: Tower frequency
How can the tower frequency affect the system?
Tower
Rotor
Controller
Tower fore-aft velocity
Thrust
Relative wind
Wind
Omega, Power
Pitch, Qg
Tower fore-aft acceleration

## Slide 18: Region 2.5: Summary
Generator speed is regulated using a PI controller on the generator torque (Kpg, Kig)

## Slide 19: Region 3: Power and speed regulation
Strategy: Regulate rotor speed by pitching and use generator torque to regulate power (either as constant power, or constant torque)

## Slide 20: Region 3: Power and speed regulation
Nonlinear equation of drivetrain motion
Generator model
PI feedback from speed error to pitch angle


## Slide 21: Region 3: Power and speed regulation
Nonlinear drive-train equation
Linear closed-loop equation for small drivetrain motion about
mass
damping
stiffness
Exercise: Derive the linearized equation and Kp,Ki
Apply the Taylor expansion to Eqn (1) and and derive the closed-loop Eqn (2)
Write Eqn (2) in the standard form (, tip: assuming ).
Derive Kp and Ki
(1)
(2)
External force

## Slide 22: Region 3: Answer
See ‘derivation.pdf’
Sometimes, we assume = 0 negligible

## Slide 23: Region 3: Aerodynamic gain scheduling
mass
damping
stiffness
External force
If Constant Torque If Constant Power
We need to maintain the closed-loop speed mode at the desired behaviour ()
However, some variables changes upon the operating point (wind speed, rotor speed, pitch angle)
How to modify our control law to ensure the desired behaviour of the closed-loop?
Cancel out
How do we know these values
This is Disturbance,

## Slide 24: How to get aerodynamic gain? Method 1
3.7 deg
= aerodynamic gain
-32 kNm/deg
-275 kW
-12 kNm/deg
Measurement from Tjæreborg turbine by Øye (1991) at rated speed of 22 rpm
When you have access to a real turbine …
Notes: Frozen wake vs steady-state gradient
Axial induction factor is frozen before reaching to a new equilibrium. This is known as dynamic inflow.

## Slide 25: How to get aerodynamic gain? Method 3
We need to calculate the steady state pitch angle
  Applying a step wind (time simulation)
  in aeroelastic code (BEM, HAWCStab2, FAST), changing the pitch until the power (aeroTorque) is reached rated.
For each pitch angle , calculate and at steady state
Now,
Repeat for next pitch
When you can only do simulation…
Notes: Steady state gradient, NOT frozen-wake gradient
Since we don’t have a dynamic inflow model

## Slide 26: Aerodynamic gain scheduling
Aerodynamic gain is the function of the operating point (wind speed, rotor speed, pitch angle)
  Rotor speed: constant at rated
  Wind speed: hard to measure
  Pitch angle: the best candidate
Implementation of :
  Look-up table: slow
  Approximation as an analytical expression:
  Linear fitting can be done by:
    least square (See code)
    Excel
    Polyfit
:Coefficient of linear term in aerodynamic gain scheduling [deg]
: Coefficient of quadratic term in aerodynamic gain scheduling [deg^2]

## Slide 27: Region 3: Gain-scheduling exercise
Now, let’s derive the aerodynamic gain from a Cp table
Exercise: Regin 3 Kp and Ki and Gain-scheduling
Run Part_5.m, that performs a step wind case and output the turbine parameter ‘turbine’ and aerodynamic gain .
Alan will go through the code
Notes: (1) Random guess of initial Kp and Ki that ensures convergence

## Slide 28: Region 3: Gain-scheduling exercise
Now you have the aerodynamic gain and turbine parameters
Exercise: Regin 3 Kp and Ki and Gain-scheduling
Calculate two set of Kp,Ki for constant torque and constant power given that . Remember that the unit for Kp and Ki are in rad/(rad/s) and rad/rad.
Enter your values in Part_5b.m
  Kp, Ki for constant torque at line 38 and 39
  KK1 and KK2 at line 51 and 52
  Kp, Ki for constant power at line 59 and 60
The code will perform three simulations (1) Constant torque without gain-scheduling (2) Constant torque (3) Constant power
What did you see? What is the trade-off between Constant Torque and Constant Power?
turbine.J: 1.5710e+08
turbine. Prated: 10000000
controller.ratedOmega: 1.0050
dQdtheta0: -2.4006e+05
KK1: 1.9835
KK2: 128.8205

## Slide 29: Region 3: Answer
Constant Torque
Kp3 = 5.0235
Ki3 = 1.1273
Constant Power
Kp3 = 5.7433
Ki3 = 1.1273
Notes: Instability if we didn’t use GS
Rotor speed similar, expected. The desired response with respect to the tuning omega and zeta
Constant power better at regulating power, however higher tower loads and more genTorq action

## Slide 30: Region 3: Summary
1. Pitch angle is determined from PI controller
2. Generator torque is either a constant (Pr/r) or to Pr/

## Slide 31: Summary
By now we should be able to:
Tune a torque PI controller in Region 2.5
Tune a pitch PI controller in Region 3
Explain how the aerodynamic gain can be calculated
Understand how gain scheduling works for Region 3