## Slide 2: Introduction to Supervisory control, advanced control topics and DTU Wind Energy Controller
Wind Turbine Control Online Course
Alan Wai Hou Lio
Researcher, DTU Wind Energy
wali@dtu.dk

## Slide 3: Re-cap
Three operational regions.
Region 2 Controller:
Transient analysis:
Region 2.5
Region 2
Region 3
Region 2
Region 2.5
Region 3
Cp

## Slide 4: Re-cap
Gain for Region 2.5
Gain for Region 3
Gain scheduling
Region 2.5
Region 2
Region 3

## Slide 5: Switching between Regions
 | Region 2 and Region 2.5 | Region 3
Generator Torque | PI with limits | Const. Torq. or Const. Pow.
Pitch | PI with limits | PI with limits
Generator Torque: PI with limits
Pitch: PI with limits
s.t.
Defined in wpdata.100
To prevent high thrust
Region 1.5

## Slide 6: Switching
Switching value between Region 2.5 and Region 3 is dependent on the pitch angle
  Pitch angle starts increasing if
  Generator torque will gradually become Const. Torq. or Const. Pow.
See code f_controller.m
(user defined)
(user defined)

## Slide 7: Anti-wind up in PID
Integral term in PI has a memory of previous error.
  How to prevent the integral term goes to infinity?
  Anti-windup strategy.
Region 2.5
Region 2
Region 3
See code f_PID_fast.m

## Slide 8: Two methods in Region 2.5
DTU: PI with limits
PI
NREL: Linear law
Hansen, M. H., & Henriksen, L. C. (2013). Basic DTU Wind Energy controller. DTU Wind Energy.
Jonkman, J., Butterfield, S., Musial, W., & Scott, G. (2009). Definition of a 5-MW Reference Wind Turbine for Offshore System Development. Golden, CO. https://doi.org/10.2172/947422

## Slide 9: Exercise: Transition Strategy
Comparison between DTU Controller and NREL Controller
Exercise: Comparison between DTU Controller and NREL Controller
Open Part_6.m
Run the script to perform a step wind speed simulation. What do you see?
Perform a turbulent wind simulation (wind_no = 3). Which one generates more energy? How about the tower loads (displacement)?

## Slide 10: Exercise: Transition Strategy
DTU: 1.1903MWh
NREL: 1.1716MWh

## Slide 11: Torque Limit
What if we let run longer?
  Can we get more power?
By default, the opening of torque limit is set to 0.95.
DTU: PI with limits

## Slide 12: Torque Limit: Step wind
Baseline: 0.6717 MWh
TorqLimit: 0.6749 MWh
But high loads

## Slide 13: Exercise: Torque Limit
Exercise: Torque limit
Open Part_8.m
The code contains two turbulent wind simulation (baseline and torque limit) at v = 12 m/s.
Increase the opening of torque limit to 0.99 at line 50. (Baseline: 0.95). Run the code
Which one generates more energy? How about the tower loads (displacement)?

## Slide 14: Start-up and shut-down
During start-up,
  Generator torque : maintains at 0 until the rotor speed reaches its minimum
  Pitch angle : maintains at optimal pitch or at some degrees to prevent large thrust.
During shut-down,
  Generator torque : linearly decreases to zero with user-defined time constant
  Pitch angle : linearly pitching out with user-defined pitch velocity

## Slide 15: Damage Equivalent Loads (DEL): Quantifying damage
Fatigue: the gradual accumulation of damage through loading cycles
Central damage concept:
  Enough load cycles of a certain amplitude cause a part to break.
Hypothesis:
  More load cycles or higher amplitudes cause faster destruction.
Research question:
  What is the relation between the amplitude of the load cycles and the number of cycles to failure?
2 material parameters: (slope) and (intercept)

## Slide 16: Damage Equivalent Loads (DEL): Cycles and damage
SN curve:
Consider load amplitude that occurs times. The accumulated damage is:
Equivalently,
We assume m=4 for metals, m=10 for composites.
Given a cyclic load, we can now calculate damage!

## Slide 17: But how to apply this to a real signal?
We need to covert a time signal to equivalent number of cycles with amplitudes.

## Slide 18: Rainflow counting
Convert time series to “peaks and valleys”.
Apply rainflow counting algorithm (rainflow() in Matlab)
The algorithm will give you:
  Number of cycles at different amplitudes

## Slide 19: DEL: Rainflow counting algorithm
Rules:
Starting from valley
  If the sequent valley is lower than the starting valley, stop and count as ½ cycle
  If not, continue the flow
Starting from peak
  If the sequent peak is higher than the starting peak, stop and count as ½ cycle
  If not, continue the flow
There exists many other methods. All of them should give you the same results.

## Slide 20: DEL: Rainflow counting algorithm
Range | Cycles
100 | 0.5
200 | 0.5
100 | 0.5
100 | 0.5
200 | 0.5
150 | 0.5
50 | 0.5
50 | 0.5
150 | 0.5
50 | 0.5
50 | 0.5
100 | 0.5
Range | Cycle
50 | 2
100 | 2
150 | 1
200 | 1
50 | 2
100 | 2
150 | 1
200 | 1
X = [0,100,-50,50,-100,75,0,50,-75,0,-50,100,0];
C = rainflow(X)
%cycles %range %mean % start %end
0.5000 100.0000 50.0000 1.0000 2.0000
1.0000 100.0000 0 3.0000 4.0000
1.0000 50.0000 25.0000 7.0000 8.0000
1.0000 50.0000 -25.0000 10.0000 11.0000
1.0000 150.0000 0 6.0000 9.0000
0.5000 200.0000 0 2.0000 5.0000
0.5000 200.0000 0 5.0000 12.0000
0.5000 100.0000 50.0000 12.0000 13.0000

## Slide 21: DEL: calculating the damage
Damage definition
Damage Equivalent Loads (DEL)
  The load amplitude that would cause the same damage given an assumed number of reference cycles.
  For 1-Hz DEL, is assumed to be the length of the signal in second
Range | Cycle
50 | 2
100 | 2
150 | 1
200 | 1
50 | 2
100 | 2
150 | 1
200 | 1
We assume m=4 for metals, m=10 for composites.
=
S = ?, n = length of signal in second
This is DEL

## Slide 22: Exercise: DEL
Exercise: Calculate the DEL of the signal
Do a rainflow flow counting on the signal by hand. i.e. do a range and cycels table
Check with Matlab if your table is correct (Matlab command: rainflow(Y))
Calculate the 1-Hz DEL based on your table, assuming m = 4.
Y = [-2,1,-3,5,-1,3,-4,4,-2];
Time [s]

## Slide 23: Answer
Range | Cycles
3 | 0.5
4 | 1.5
6 | 0.5
8 | 1
9 | 0.5
DEL: ((3^4*0.5+4^4*1.5+6^4*0.5+8^4*1+9^4*0.5)/9)^(1/4) = 5.5353

## Slide 24: Peak shaving
Peak thrust load is at maximum around rated wind speed.
Thrust can be reduced by increasing the pitch
How to implement?
  Change the minimum pitch angle
  In wpdata.100

## Slide 25: Exercise: Peak shaving
Exercise: Peak shaving
Open Part_7.m and run a steady-state plots of power, thrust, pitch and rotor speed
Modify wpdata_DTU10MW_Part7.100 file with your chosen pitch angles.
Run Part_7b.m to see the steady-state of your design. Your chosen pitch angles needs to make the thrust within 1.3MN.
Run Part_7c.m to perform a turbulent wind simulation. Do you see a trade-off between power and tower loads?

## Slide 26: Exercise: Peak shaving
Blue: Baseline [0.7997 MWh]
Red: Peak shaving [0.7931 MWh]

## Slide 27: Advanced Control topics: Control of tower fore-aft vibration
Tower fore-aft mode is lightly damped
Feedback loop mapping tower velocity to pitch angle
Rotor thrust varies rapidly around rated wind speed with pitch angle close to fine pitch
Solution: Limited the negative pitch rate when close to fine pitch
Wind Turbine
Basic Controller

## Slide 28: Advanced Control topics: Control of drive-train torsional vibration
Torsional vibration is coupled with the first blade-edgewise mode
At above-rated wind region, the generator torque is designed to dampen the torsional vibration
A band-pass filter is used
Wind Turbine
Basic Controller
Band-pass filter

## Slide 29: Advanced Control topics: Individual Pitch Control
Turbines are subject to periodic loadings:
  Wind shear, tower shadow
Cyclic pitch control: azimuth-dependent change to the demand pitch angle for each blade
Turbulent variations in wind speed across a large turbine rotor dominates the asymmetrical loadings.
  Individual Pitch Control:
  Use load sensor to measure blade bending moment
  Adjust the blade individually